## M Series
Model Reference |  | Cooling Performance |  |  |  |  | Heating Performance |  |  | Airflow |  | Indoor Unit |  |  |  |  | Outdoor Unit |  |  | Electrical | [5 empty] | Refrigerant | [5 empty] | Others |  | Guaranteed Operating Range
|  | Nominal Total Cooling*1 | Nominal Sensible Cooling*1 | Rated Sensible Cooling*1 | AEER/EER | Star Rating | Nominal Heating Capacity*1 | ACOP/COP | Star Rating | Airflow (Cooling/Heating) | Ext. Static Pressure | Dimensions (H x W x D) | Supply Spigot Size (H x W) | Return Spigot Size (H x W) | Unit Weight | Noise Level (SPL/PWL) - in Cooling | Dimensions (H x W x D) | Weight | Noise Level (SPL/PWL) - in Cooling | Volt / Phase | MCA | MCB | RLA (Cooling/ Heating)*2 | Power Supply to OU*3 | IU/OU Connecting Wire | Pipe Size (Gas) OD | Pipe Size (Liquid) OD | Max Pipe Run | Max Lift | Pre-Charged R410A | Add. Charge | Drain Pumps | Standard Accessories | Indoor - Cooling | Indoor - Heating | Outdoor - Cooling | Outdoor - Heating
|  | kW | kW | kW |  |  | kW |  |  | L/s | Pa | mm | mm | mm | kg | dB(A) | mm | kg | dB(A) |  | A | A | A |  |  | mm (Inch) | mm (Inch) | m | m | kg | g/m |  |  | °CDB/°CWB | °CDB | °CDB | °CDB/°CWB
Deluxe Wall Mounted MSZ-FB Series
| MSZ-FB25VA MUZ-FB25VA | 2.5 (1.1-3.5) | 2.46 | 2.4 | 4.53/4.76 | 4.5 | 3.2 (1.5-5.5) | 4.69/4.89 | 5 | 77-187 | - | 295 x 798 x 257 | - | - | 12 | 20-29-36-42 | 550 x 800 x 285 | 36 | 46/59 | 240/1 | 10 | 10 | 2.6/3.1 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.15 (7.0 m) | 30 | N/A | Wireless control included | 21/15 to 32/23 | 20 to 27 | -10 to 46 | -15/16 to 24/18
Signature Wall Mounted MSZ-EF Series
| MSZ-EF22VEW/B/S (MXZ only) | 2.2 | - | - | - | - | - | - | - | 67-175/67-198 | - | 299 x 895 x 195 | - | - | 11.5 | 21-23-39-36-42 | Refer to MXZ |  |  | Refer to MXZ | [5 empty] | 9.52 (3/8) | 6.35 (1/4) | Refer to MXZ |  |  |  | N/A | Wireless control included*6*7 | 21/15 to 32/23 | 20 to 27 | Refer to MXZ
| MSZ-EF25VEW/B/S MUZ-EF25VE | 2.5 (1.2-3.4) | 2.31 | 2.25 | 4.56/4.59 | 4.5 | 3.2 (1.1-4.2) | 4.55/4.57 | 4.5 | 67-175/67-198 | - | 299 x 895 x 195 | - | - | 11.5 | 21-23-29-36-42 | 550 x 800 x 285 | 30 | 47/60 | 240/1 | 7.3 | 10 | 2.9/3.5 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 0.8 (7.0 m) | 30 | N/A | Wireless control included*6*7 |  |  | -10 to 46 | -15/16 to 24/18
| MSZ-EF35VEW/B/S MUZ-EF35VE | 3.5 (1.4-4.0) | 2.81 | 2.74 | 3.83/3.85 | 3 | 4.0 (1.8-5.5) | 4.17/4.19 | 4 | 67-175/67-212 | - | 299 x 895 x 195 | - | - | 11.5 | 21-24-29-36-42 | 550 x 800 x 285 | 35 | 49/63 | 240/1 | 8.5 | 10 | 4.2/4.4 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.15 (7.0 m) | 30 | N/A | Wireless control included*6*7
| MSZ-EF42VEW/B/S MUZ-EF42VE | 4.2 (0.9-4.6) | 3.04 | 2.96 | 3.27/3.28 | 2 | 5.4 (1.4-6.3) | 3.69/3.70 | 2.5 | 97-172/92-212 | - | 299 x 895 x 195 | - | - | 11.5 | 28-31-35-39-42 | 550 x 800 x 285 | 35 | 50/64 | 240/1 | 9.5 | 10 | 5.7/6.5 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.15 (7.0 m) | 30 | N/A | Wireless control included*6*7
| MSZ-EF50VEW/B/S MUZ-EF50VE | 5.0 (1.4-5.4) | 3.57 | 3.47 | 3.20/3.21 | 1.5 | 5.8 (1.6-7.5) | 3.70/3.71 | 2.5 | 97-183/107-220 | - | 299 x 895 x 195 | - | - | 11.5 | 30-33-36-40-43 | 850 x 840 x 330 | 54 | 52/66 | 240/1 | 12.4 | 16 | 6.9/7.0 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 15 | 1.15 (7.0 m) | 20 | N/A | Wireless control included*6*7
Classic Wall Mounted MSZ-GE Series
| MSZ-GE22VAD (MXZ only) | 2.2 | - | - | - | - | - | - | - | 68-188/68-192 | - | 295 x 798 x 232 | - | - | 10 | 19-21-29-36-42 | Refer to MXZ |  |  | Refer to MXZ | [5 empty] | 9.52 (3/8) | 6.35 (1/4) | Refer to MXZ |  |  |  | N/A | Wireless control included*6 | 21/15 to 32/23 | 20 to 27 | Refer to MXZ
| MSZ-GE25VAD MUZ-GE25VAD | 2.5 (1.1-3.5) | 2.41 | 2.35 | 4.21/4.46 | 4 | 3.2 (1.3-4.1) | 4.19/4.38 | 4 | 68-188/68-192 | - | 295 x 798 x 232 | - | - | 10 | 19-21-29-36-42 | 550 x 800 x 285 | 30 | 46/58 | 240/1 | 7.4 | 10 | 2.9/3.8 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 0.8 (7.0 m) | 30 | N/A | Wireless control included*6 |  |  | -10 to 46 | -15/16 to 24/18
| MSZ-GE35VAD MUZ-GE35VAD | 3.5 (1.1-4.0) | 2.99 | 2.91 | 3.67/3.80 | 3 | 4.0 (1.6-5.3) | 3.91/4.04 | 3.5 | 68-212/68-192 | - | 295 x 798 x 232 | - | - | 10 | 19-22-30-36-43 | 550 x 800 x 285 | 33 | 47/61 | 240/1 | 8.6 | 10 | 4.4/4.6 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.15 (7.0 m) | 30 | N/A | Wireless control included*6
| MSZ-GE42VAD MUZ-GE42VAD | 4.2 (0.9-4.8) | 3.25 | 3.16 | 3.25/3.33 | 2 | 5.4 (1.4-6.0) | 3.43/3.51 | 2.5 | 97-213/97-218 | - | 295 x 798 x 232 | - | - | 10 | 26-30-35-40-46 | 550 x 800 x 285 | 36 | 50/62 | 240/1 | 10 | 10 | 5.8/7.0 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.15 (7.0 m) | 30 | N/A | Wireless control included*6
| MSZ-GE50VAD MUZ-GE50VAD | 5.0 (1.4-5.4) | 3.82 | 3.72 | 3.17/3.24 | 2 | 5.8 (1.4-7.2) | 3.44/3.52 | 2.5 | 108-252/108-242 | - | 295 x 798 x 232 | - | - | 10 | 28-33-38-44-49 | 850 x 840 x 330 | 54 | 54/69 | 240/1 | 13 | 16 | 6.8/7.4 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 15 | 1.15 (7.0 m) | 20 | N/A | Wireless control included*6
| MSZ-GE60VAD MUZ-GE60VAD | 6.0 (1.5-7.5) | 4.71 | 4.58 | 3.37/3.41 | 2.5 | 6.8 (2.0-9.3) | 3.80/3.84 | 3 | 163-305 |  | 325 x 1100 x 238 | - | - | 16 | 29-37-41-45-49 | 880 x 840 x 330 | 50 | 55/69 | 240/1 | 14.5 | 20 | 7.8/7.8 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 6.35 (1/4) | 30 | 15 | 1.15 (7.0 m) | 20 | N/A | Wireless control included*6*7
| MSZ-GE71VAD MUZ-GE71VAD | 7.1 (2.4-8.7) | 5.64 | 5.48 | 3.30/3.33 | 2 | 8.1 (2.2-9.9) | 3.80/3.84 | 3 | 170-298 |  | 325 x 1100 x 238 | - | - | 16 | 30-37-41-45-49 | 880 x 840 x 330 | 53 | 55/69 | 240/1 | 16.6 | 20 | 9.4/9.5 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 15 | 1.90 (10.0 m) | 55 | N/A | Wireless control included*6*7
| MSZ-GE80VAD MUZ-GE80VAD | 8.0 (2.4-9.2) | 6.03 | 5.87 | 3.14/3.17 | 2 | 9.0 (2.2-11.1) | 3.50/3.53 | 2.5 | 170-298 |  | 325 x 1100 x 238 | - | - | 16 | 30-37-41-45-49 | 880 x 840 x 330 | 53 | 55/69 | 240/1 | 16.6 | 20 | 10.8/11.2 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 15 | 1.90 (10.0 m) | 55 | N/A | Wireless control included*6*7
Floor Standing MFZ Series
| MFZ-KJ25VE MUFZ-KJ25VE | 2.5 (0.5-3.4) | 1.63 | 1.59 | 4.62/4.63 | 5 | 3.4 (1.2-4.6) | 4.41/4.42 | 4 | 65-82-98-118-137 | - | 600 x 750 x 215 | - | - | 15 | 20-39 | 550 x 800 x 285 | 37 | 46/59 | 240/1 | 9.4 | 10 | 2.7/3.7 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.1 (7.0 m) | 30 | N/A | Wireless control included*6*7 | 21/15 to 32/23 | 20 to 27 | -10 to 46 | -15/16 to 24/18
| MFZ-KJ35VE MUFZ-KJ35VE | 3.5 (0.5-3.7) | 2.29 | 2.22 | 3.88/3.89 | 3 | 4.3 (1.2-5.8) | 3.90/3.91 | 3 | 65-82-98-118-137 | - | 600 x 750 x 215 | - | - | 15 | 20-39 | 550 x 800 x 285 | 37 | 47/60 | 240/1 | 9.4 | 10 | 4.2/5.0 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.1 (7.0 m) | 30 | N/A | Wireless control included*6*7
| MFZ-KJ50VE MUFZ-KJ50VE | 5.0 (1.6-5.7) | 3.17 | 3.08 | 3.56/3.57 | 2.5 | 5.8 (2.2-8.2) | 3.86/3.87 | 3 | 93-112-113-155-177 | - | 600 x 750 x 215 | - | - | 15 | 27-44 | 880 x 840 x 330 | 55 | 49/63 | 240/1 | 14 | 16 | 6.2/6.7 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 15 | 1.5 (7.0 m) | 20 | N/A | Wireless control included*6*7
| MFZ-KJ60VE MUFZ-KJ60VE | 6.0 (1.6-6.8) | 3.8 | 3.7 | 3.42/3.43 | 2 | 6.8 (2.2-9.1) | 3.59/3.6 | 2.5 | 93-133-160-205-250 | - | 600 x 750 x 215 | - | - | 15 | 27-53 | 880 x 840 x 330 | 55 | 52/65 | 240/1 | 16.5 | 20 | 7.8/8.4 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 15 | 1.5 (7.0 m) | 20 | N/A | Wireless control included*6*7
Compact Ceiling Cassette SLZ Series
| SLZ-KA25VAQ/L SUZ-KA25VA3 | 2.3 (0.9-3.2) | 2.21 | 2.1 | 3.65/3.83 | 2.5 | 3.1 (0.9-4.5) | 3.66/3.78 | 3 | 133-150-167 | - | 208 x 570 x 570 | - | - | 16.5 | 28-31-37 | 550 x 800 x 285 | 30 | 46 | 240/1 | 8.16 | 10 | 2.9/3.9 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 0.8 (5.0 m) | 30 | Standard (500 mm lift) | VAL includes wireless control *8 | 21/15 to 32/23 | 20 to 27 | -10 to 46 | -10/-11 to 24/18
| SLZ-KA35VAQ/L (MXZ only) | 3.5 | 2.77 | 2.53 | - | - | 4 | - | - | 133-150-183 | - | 208 x 570 x 570 | - | - | 16.5 | 29-33-38 | Refer to MXZ |  |  | Refer to MXZ | [5 empty] | 9.52 (3/8) | 6.35 (1/4) | Refer to MXZ |  |  |  | Standard (500 mm lift) | VAL includes wireless control *8 |  |  | Refer to MXZ
| SLZ-KA50VAQ/L SUZ-KA50VA3 | 4.2 (1.1-5.2) | 2.94 | 2.8 | 3.23/3.31 | 2 | 4.5 (0.9-6.5) | 3.22/3.28 | 1.5 | 133-150-183 | - | 208 x 570 x 570 | - | - | 16.5 | 30-34-39 | 550 x 800 x 285 | 53 | 55 | 240/1 | 16 | 20 | 5.8/6.2 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 15 | 1.6 (7.0 m) | 20 | Standard (500 mm lift) | VAL includes wireless control *8 |  |  | -10 to 43 | -10/-11 to 24/18
Compact Ceiling Concealed SEZ Series
| SEZ-KD25VAQ/L SUZ-KA25VA3 | 2.5 (0.9-3.2) | 2 | 1.9 | 3.21/3.33 | - | 3.0 (0.9-4.5) | 3.49/3.61 | - | 92-117-150 | 5-15-35-50 | 200 x 790 x 700 | 150 x 660 | 157.5 x 660 | 18 | 23-26-30 | 550 x 800 x 285 | 30 | 46 | 240/1 | 8.16 | 10 | 3.6/4.0 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 0.8 (5.0 m) | 30 | Optional*5 | VAL includes wireless control*9 | 21/15 to 32/23 | 20 to 27 | -10 to 46 | -10/-11 to 24/18
| SEZ-KD35VAQ/L SUZ-KA35VA2 | 3.7 (1.0-3.9) | 2.81 | 2.67 | 3.31/3.39 | - | 4.2 (0.9-5.0) | 3.62/3.72 | - | 117-150-183 | 5-15-35-50 | 200 x 990 x 700 | 150 x 860 | 157.5 x 860 | 21 | 23-28-33 | 550 x 800 x 285 | 33 | 48 | 240/1 | 9.18 | 10 | 5.1/5.2 | 3C | SDI + TPS (2C+E)*4 | 9.52 (3/8) | 6.35 (1/4) | 20 | 12 | 1.05 (5.0 m) | 30 | Optional*5 | VAL includes wireless control*9
| SEZ-KD50VAQ/L SUZ-KA50VA3 | 5.1 (1.1-5.6) | 3.88 | 3.69 | 3.05/3.11 | - | 6.4 (1.1-7.2) | 3.48/3.54 | - | 167-208-250 | 5-15-35-50 | 200 x 990 x 700 | 150 x 860 | 157.5 x 860 | 23 | 30-34-37 | 850 x 840 x 330 | 53 | 55 | 240/1 | 16 | 20 | 7.4/8.2 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 30 | 1.6 (7.0 m) | 20 | Optional*5 | VAL includes wireless control*9
| SEZ-KD60VAQ/L SUZ-KA60VA3 | 5.6 (1.1-6.3) | 4.43 | 4.21 | 3.11/3.16 | - | 7.4 (0.9-8.0) | 3.55/3.61 | - | 200-250-300 | 5-15-35-50 | 200 x 1190 x 700 | 150 x 1060 | 157.5 x 1060 | 27 | 30-34-38 | 880 x 840 x 330 | 50 | 55 | 240/1 | 14 | 20 | 7.9/9.1 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 6.35 (1/4) | 30 | 30 | 1.8 (7.0 m) | 20 | Optional*5 | VAL includes wireless control*9
| SEZ-KD71VAQ/L SUZ-KA71VA3 | 6.5 (0.9-8.3) | 5.07 | 4.82 | 3.10/3.16 | - | 8.1 (0.9-10.4) | 3.66/3.72 | - | 200-267-333 | 5-15-35-50 | 200 x 1190 x 700 | 150 x 1060 | 157.5 x 1060 | 27 | 30-35-40 | 880 x 840 x 330 | 53 | 55 | 240/1 | 16.1 | 20 | 9.2/9.7 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 30 | 1.8 (7.0 m) | 55 | Optional*5 | VAL includes wireless control*9
Notes:
*1 - Nominal conditions cooling: EAT 27°CDB/19°CWB, Ambient 35°CDB | [9 empty] | mm: *5 - Optional drain pump for SEZ series: PAC-KE07DM-E | [10 empty] | Mitsubishi Electric is constantly developing and improving its products. The company reserves the right to make any variation in the technical specification to the equipment described, or to withdraw or replace products without prior notification. This is a guide only, please refer to the installation and service manuals to confirm the latest specifications or contact your local Mitsubishi Electric office.
Rated conditions cooling: EAT 24°CDB/17°CWB, Ambient 35°CDB | [9 empty] | mm: *6 - Optional wi-fi control: MAC-558-IF-E
Nominal conditions heating: EAT 20°CDB/15°CWB, Ambient 7°CDB/6°CWB | [9 empty] | mm: *7 - Standard Wireless controller with 7-day schedule
*2 - Rated Load Amps (RLA) is based on nominal conditions. Use Maximum Circuit Amps (MCA) for power supply infrastructure sizing, etc. | [9 empty] | mm: *8 - Grille for SLZ-KA VAL series (wireless option): SLP-2ALW
*3 - 3-core (3C) electrical power supply cable to outdoor unit only, indoor unit is fed from outdoor unit. | [9 empty] | mm: Grille for SLZ-KA VAQ series (wired option): SLP-2AAW (add wired controller PAR-31MAA or PAC-YT52CRA)
*4 - Single core double insulated (SDI) and Thermoplastic Sheated (TPS) twin and earth (2C+E) | [9 empty] | mm: *9 - For VAQ model, add wired controller PAR-31MAA or PAC-YT52CRA

## MXZ-Series
Model Reference |  | Connectable Indoor Unit |  |  | Performance |  |  |  |  | Outdoor Unit |  |  | Electrical | [5 empty] | Refrigerant | [5 empty] | Guaranteed Operating Range
|  | No. Connectable Indoor Unit | Max Connectable Total IU Capacity | Largest Connectable IU | Cooling Capacity*1 | AEER/EER | Heating Capacity*1 | ACOP/COP | Airflow (Cooling/ Heating) | Dimensions (H x W x D) | Weight | Noise Level (SPL) - in Cooling/Heating | Volt / Phase | MCA | MCB | RLA (Cooling/ Heating)*2 | Power Supply to OU*3 | IU/OU Connecting Wire | Pipe Size (Gas) OD | Pipe Size (Liquid) OD | Max Run (Each IU/Total) | Max Lift | Pre-Charged R410A (Limit) | Add. Charge | Outdoor - Cooling | Outdoor - Heating
|  | (Min - Max) | kW | kW | kW |  | kW |  | L/s | mm | kg | dB(A) |  | A | A | A |  |  | mm (Inch) | mm (Inch) | m | m | kg | g/m | °CDB | °CDB/°CWB
Multi Head Outdoor MXZ Series
| MXZ-2D52VA | 2 | 7 | 3.5 | 5.2 | 3.67/3.71 | 6.1 | 3.80/3.84 | 525/ 532 | 550 x 800 x 285 | 37 | 50/53 | 240/1 | 10.2 | 20 | 6.3/7.1 | 3C | SDI + TPS (2C+E)*4 | 2 x 6.35 (1/4) | 2 x 9.52 (3/8) | 20/30 | 15 | 1.3 (20.0 m) | 20 | -10 to 46 | -15 to 24
| MXZ-3D54VA | 2 - 3 | 9.5 | 5 | 5.4 | 3.95/4.32 | 7 | 4.06/4.35 | 649/ 754 | 710 x 840 x 330 | 57 | 50/53 | 240/1 | 15 | 20 | 5.5/7.1 | 3C | SDI + TPS (2C+E)*4 | 3 x 6.35 (1/4) | 3 x 9.52 (3/8) | 25/50 | 15 | 2.7 (40.0 m) | 20 | -10 to 46 | -15 to 24
| MXZ-4D71VA | 2 - 4 | 12 | 6 | 7.1 | 3.50/3.78 | 8 | 4.03/4.35 | 649/ 778 | 710 x 840 x 330 | 58 | 50/54 | 240/1 | 15 | 25 | 8.3/8.1 | 3C | SDI + TPS (2C+E)*4 | 4 x 6.35 (1/4) | 1 x 12.7 (1/2) + 3 x 9.52 (3/8) | 25/60 | 15 | 2.7 (40.0 m) | 20 | -10 to 46 | -15 to 24
| MXZ-4D80VA | 2 - 4 | 14 | 7.1 | 8 | 3.59/3.86 | 8.8 | 3.86/4.13 | 910/ 833 | 915 x 900 x 320 | 69 | 51/51 | 240/1 | 17.4 | 25 | 9.1/9.4 | 3C | SDI + TPS (2C+E)*4 | 4 x 6.35 (1/4) | 1 x 12.7 (1/2) + 3 x 9.52 (3/8) | 25/70 | 15 | 3.5 (40.0 m) | 20 | -10 to 46 | -15 to 24
| MXZ-5D100VA | 2 - 5 | 17 | 7.1 | 10 | 3.07/3.24 | 10 | 3.58/3.80 | 974/ 1050 | 915 x 900 x 320 | 70 | 53/59 | 240/1 | 18.4 | 25 | 13.6/11.6 | 3C | SDI + TPS (2C+E)*4 | 4 x 6.35 (1/4) | 1 x 12.7 (1/2) + 4 x 9.52 (3/8) | 25/80 | 15 | 4.0 (40.0 m) | 20 | -10 to 46 | -15 to 24
| MXZ-6D120VA | 2 - 6 | 18 | 8.0 (MSZ-GE) | 12 | 3.18/3.32 | 13.5 | 3.45/3.60 | 987/ 1158 | 1070 x 900 x 320 | 87 | 53/57 | 240/1 | 27 | 32 | 15.9/16.5 | 3C | SDI + TPS (2C+E)*4 | 6 x 6.35 (1/4) | 1 x 12.7 (1/2) + 5 x 9.52 (3/8) | 25/80 | 15 | 4.8 (60.0 m) | 20 | -10 to 46 | -15 to 24
Power Multi Outdoor MXZ Series
| MXZ-8B140VA | 2 - 8 | 18.5 | 10.0 (PLA, PEAD)* | 14 | 3.52 | 16 | 3.91 | 1667 | 1350 x 950 x 330 | 129 | 50/52 | 240/1 | 29.5 | 40 | 16.6/17.1 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 15 (BC-IU); 70 (OU-IU)/115 | 15 (BC-IU); 30 (OU-IU) | 8.5 (40.0 m) | Refer to Manual | -5 to 46 | -15 to 21
| MXZ-8B160VA | 2 - 8 | 20.2 | 10.0 (PLA, PEAD)* | 15.5 | 3.21 | 18 | 3.61 | 1767 | 1350 x 950 x 330 | 129 | 51/54 | 240/1 | 29.5 | 40 | 20.4/21.1 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 15 (BC-IU); 70 (OU-IU)/115 | 15 (BC-IU); 30 (OU-IU) | 8.5 (40.0 m) | Refer to Manual | -5 to 46 | -15 to 21
Power Multi Branch Box
| PAC-AK32BC | 3 |  |  | - | - | - | - | - | 198 x 450 x 280 | 8.1 | - | - | - | - | - | Fed from OU | SDI + TPS (2C+E)*4 | 3 x 9.52 (3/8) | 3 x 6.35 (1/4) | - | - | - | - | - | -
| PAC-AK53BC | 5 |  |  | - | - | - | - | - | 198 x 450 x 280 | 9.3 | - | - | - | - | - | Fed from OU | SDI + TPS (2C+E)*4 | 1 x 12.7 (1/2) + 4 x 9.52 (3/8) | 5 x 6.35 (1/4) | - | - | - | - | - | -
Notes:
*1 - Nominal conditions cooling: EAT 27°CDB/19°CWB, Ambient 35°CDB
Nominal conditions heating: EAT 20°CDB/15°CWB, Ambient 7°CDB/6°CWB
*2 - Rated Load Amps (RLA) is based on nominal conditions. Use Maximum Circuit Amps (MCA) for power supply infrastructure sizing, etc. | [18 empty] | Mitsubishi Electric is constantly developing and improving its products. The company reserves the right to make any variation in the technical specification to the equipment described, or to withdraw or replace products without prior notification. This is a guide only, please refer to the installation and service manuals to confirm the latest specifications or contact your local Mitsubishi Electric office.
*3 - 3-core (3C) electrical power supply cable to outdoor unit only, indoor unit is fed from outdoor unit.
*4 - Single core double insulated (SDI) and Thermoplastic Sheated (TPS) twin and earth (2C+E)

## Mr Slim
Model Reference |  | Cooling Performance |  |  |  | Heating Performance |  | Airflow | Indoor Unit |  |  | Outdoor Unit |  |  | Electrical | [5 empty] | Refrigerant | [5 empty] | Others |  | Guaranteed Operating Range
|  | Nominal Total Cooling*1 | Nominal Sensible Cooling*1 | Rated Sensible Cooling*1 | AEER/EER | Nominal Heating Capacity*1 | ACOP/COP | Airflow (Cooling/Heating) | Dimensions (H x W x D) | Weight | Noise Level (SPL/PWL) - in Cooling | Dimensions (H x W x D) | Weight | Noise Level (SPL/PWL) - in Cooling | Volt / Phase | MCA | MCB | RLA (Cooling/ Heating)*2 | Power Supply to OU*3 | IU/OU Connecting Wire | Pipe Size (Gas) OD | Pipe Size (Liquid) OD | Max Run | Max Lift | Pre-Charged R410A (Limit) | Add. Charge | Drain Pumps | Standard Accessories | Indoor - Cooling | Indoor - Heating | Outdoor - Cooling | Outdoor - Heating
|  | kW | kW | kW |  | kW |  | L/s | mm | kg | dB(A) | mm | kg | dB(A) |  | A | A | A |  |  | mm (Inch) | mm (Inch) | m | m | kg | g/m |  |  | °CDB/°CWB | °CDB | °CDB | °CDB/°CWB
Wall Mounted PKA Series Power Inverter
| PKA-RP71KAL PUHZ-RP71VHA5 | 7.1 (3.3-8.1) | 5.7 | 5.21 | 3.42/3.62 | 8.0 (3.5-10.2) | 3.56/3.76 | 300-333-367 | 365 x 1170 x 295 | 21 | 39-42-45 | 943 x 950 x 330 | 67 | 48 | 240/1 | 19.5 | 25 | 9.05/9.64 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 50 | 30 | 3.5 (30.0 m) | 600 per 10 m | Optional*5 | Wireless control included*7 | 19 / 15 to 35 / 22.5 | 17 to 28 | -5 (-15) to 46 | -20 / -20 to 21 / 15
| PKA-RP100KAL PUHZ-RP100VKA2 | 10.0 (4.9-11.4) | 7.51 | 6.87 | 3.20/3.45 | 11.2 (4.5-14.0) | 3.34/3.61 | 333-383-433 | 365 x 1170 x 295 | 21 | 41-45-49 | 1338 x 1050 x 330 | 118 | 51 | 240/1 | 27.2 | 32 | 12.64/13.58 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Wireless control included*7
| PKA-RP100KAL PUHZ-RP100YKA2 | 10.0 (4.9-11.4) | 7.51 | 6.87 | 3.17/3.45 | 11.2 (4.5-14.0) | 3.31/3.61 | 333-383-433 | 365 x 1170 x 295 | 21 | 41-45-49 | 1338 x 1050 x 330 | 119 | 51 | 415/3 | 8.7 | 16 | 4.42/4.75 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Wireless control included*7
Ceiling Cassette PLA Series Power Inverter
| PLA-RP60BAR1 SUZ-KA60VAD | 6.1 (1.1-6.3) | 4.64 | 4.41 | 3.36/3.43 | 6.9 (0.9-8.0) | 3.44/3.50 | 200-233-267-300 | 258 x 840 x 840 | 23 | 28-29-31-32 | 880 x 840 x 330 | 50 | 55 | 240/1 | 14 | 20 | 7.9/8.7 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 6.35 (1/4) | 30 | 30 | 1.8 (7.0 m) | 20 | Standard (850 mm) | Wireless/ wired controller and facia option*6 | 21 /15 to 32 / 23 | 20 to 27 | -10 to 43 | -10 / -11 to 24 / 18
| PLA-RP71BAR1 SUZ-KA71VAD | 7.1 (0.9-8.1) | 5.19 | 4.93 | 3.38/3.43 | 8.0 (0.9-10.2) | 3.60/3.65 | 233-267-300-350 | 258 x 840 x 840 | 23 | 28-30-32-34 | 880 x 840 x 330 | 53 | 55 | 240/1 | 16.1 | 20 | 9.2/9.7 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 30 | 1.8 (7.0 m) | 55 | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-RP71BAR1 PUHZ-RP71VHA5 | 7.3 (3.3-8.1) | 5.33 | 4.87 | 3.22/3.40 | 8.0 (3.5-10.2) | 3.49/3.69 | 233-267-300-350 | 258 x 840 x 840 | 23 | 28-30-32-34 | 943 x 950 x 330 | 67 | 48 | 240/1 | 19.5 | 20 | 9.05/9.64 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 50 | 30 | 3.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6 | 19 / 15 to 35 / 22.5 | 17 to 28 | -5 (-15) to 46 | -20 / -20 to 21 / 15
| PLA-RP100BA PUHZ-RP100VKA2 | 10 (4.9-11.4) | 7.61 | 6.96 | 3.67/4.00 | 11.2 (4.5-14.0) | 3.54/3.80 | 334-384-434-501 | 298 x 840 x 840 | 25 | 32-34-37-40 | 1338 x 1050 x 330 | 118 | 51 | 240/1 | 26.5 | 32 | 12.64/13.58 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-RP100BA PUHZ-RP100YKA2 | 10 (4.9-11.4) | 7.61 | 6.96 | 3.63/4.00 | 11.2 (4.5-14.0) | 3.50/3.80 | 334-384-434-501 | 298 x 840 x 840 | 25 | 32-34-37-40 | 1338 x 1050 x 330 | 119 | 51 | 415/3 | 8 | 16 | 4.42/4.75 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-125BA PUHZ-RP125VKA2 | 12.5 (5.5-14.0) | 9.13 | 8.35 | 3.10/3.29 | 14.0 (5.0-16.0) | 3.56/3.77 | 367-417-467-517 | 298 x 840 x 840 | 25 | 34-36-39-41 | 1338 x 1050 x 330 | 118 | 52 | 240/1 | 26.5 | 32 | 16.36/16.90 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-125BA PUHZ-RP125YKA2 | 12.5 (5.5-14.0) | 9.13 | 8.35 | 3.08/3.29 | 14.0 (5.0-16.0) | 3.54/3.77 | 367-417-467-517 | 298 x 840 x 840 | 25 | 34-36-39-41 | 1338 x 1050 x 330 | 119 | 52 | 415/3 | 9.5 | 16 | 5.73/5.91 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-RP140BA PUHZ-RP140VKA2 | 13.0 (6.2-15.3) | 9.89 | 9.05 | 3.10/3.27 | 16.0 (5.7-18.0) | 3.44/3.61 | 400-434-484-534 | 298 x 840 x 840 | 27 | 36-39-42-44 | 1338 x 1050 x 330 | 120 | 52 | 240/1 | 28 | 40 | 17.17/19.23 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
| PLA-RP140BA PUHZ-RP140YKA2 | 13.0 (6.2-15.3) | 9.89 | 9.05 | 3.08/3.27 | 16.0 (5.7-18.0) | 3.42/3.61 | 400-434-484-534 | 298 x 840 x 840 | 27 | 36-39-42-44 | 1338 x 1050 x 330 | 121 | 52 | 415/3 | 13 | 16 | 6.01/6.73 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Standard (850 mm) | Wireless/ wired controller and facia option*6
Under Ceiling PCA Series Power Inverter
| PCA-RP50KAQ SUZ-KA50VAD | 4.9 (1.1-5.6) | 3.83 | 3.63 | 3.22/3.29 | 5.5 (0.9-6.6) | 3.22/3.27 | 167-183-217-250 | 230 x 960 x 680 | 25 | 32-34-37-40 | 850 x 840 x 330 | 53 | 55 | 240/1 | 16 | 20 | 6.80/7.60 | 3C | SDI + TPS (2C+E)*4 | 12.7 (1/2) | 6.35 (1/4) | 30 | 30 | 1.6 (7.0 m) | 20 | Optional*5 | Optional controller*7 | 21 / 15 to 32 / 23 | 20 to 27 | -10 to 43 | -10 / -11 to 24 / 18
| PCA-RP60KAQ SUZ-KA60VAD | 5.7 (1.1-6.3) | 4.62 | 4.39 | 3.35/3.41 | 6.9 (0.9-8.0) | 3.36/3.42 | 250-267-283-317 | 230 x 1280 x 680 | 32 | 33-35-37-40 | 880 x 840 x 330 | 50 | 55 | 240/1 | 14 | 20 | 7.40/9.00 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 6.35 (1/4) | 30 | 30 | 1.8 (7.0 m) | 20 | Optional*5 | Optional controller*7
| PCA-RP71KAQ SUZ-KA71VAD | 7.1 (0.9-8.1) | 5.4 | 5.13 | 3.39/3.45 | 7.9 (0.9-10.2) | 3.96/4.03 | 267-283-300-333 | 230 x 1280 x 680 | 32 | 35-37-39-41 | 880 x 840 x 330 | 53 | 55 | 240/1 | 16.1 | 20 | 9.10/8.70 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 30 | 1.8 (7.0 m) | 55 | Optional*5 | Optional controller*7
| PCA-RP71KAQ PUHZ-RP71VHA5 | 7.3 (3.3-8.1) | 5.55 | 5.08 | 3.42/3.62 | 8.0 (3.5-10.2) | 3.44/3.62 | 267-283-300-333 | 230 x 1280 x 680 | 32 | 35-37-39-41 | 943 x 950 x 330 | 67 | 48 | 240/1 | 19.5 | 25 | 9.05/9.64 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 50 | 30 | 3.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7 | 19 / 15 to 35 / 22.5 | 17 to 28 | -5 (-15) to 46 | -20 / -20 to 21 / 15
| PCA-RP100KAQ PUHZ-RP100VKA2 | 10.28 (4.9-11.4) | 7.92 | 7.24 | 3.50/3.80 | 11.2 (4.5-14.0) | 3.46/3.71 | 367-400-433-467 | 230 x 1600 x 680 | 36 | 37-39-41-43 | 1338 x 1050 x 330 | 118 / 119 | 51 | 240/1 | 26.5 | 32 | 12.64/13.58 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
| PCA-RP100KAQ PUHZ-RP100YKA2 | 10.28 (4.9-11.4) | 7.92 | 7.24 | 3.47/3.80 | 11.2 (4.5-14.0) | 3.43/3.71 | 367-400-433-467 | 230 x 1600 x 680 | 36 | 37-39-41-43 | 1338 x 1050 x 330 | 118 / 119 | 51 | 415/3 | 8 | 16 | 4.42/4.75 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
| PCA-RP125KAQ PUHZ-RP125VKA2 | 12.34 (5.5-14.0) | 9.5 | 8.69 | 3.09/3.28 | 14.0 (5.0-16.0) | 3.41/3.61 | 383-417-450-483 | 230 x 1600 x 680 | 38 | 39-41-43-45 | 1338 x 1050 x 330 | 118 / 119 | 52 | 240/1 | 26.5 | 32 | 16.36/16.90 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
| PCA-RP125KAQ PUHZ-RP125YKA2 | 12.34 (5.5-14.0) | 9.5 | 8.69 | 3.07/3.28 | 14.0 (5.0-16.0) | 3.39/3.61 | 383-417-450-483 | 230 x 1600 x 680 | 38 | 39-41-43-45 | 1338 x 1050 x 330 | 118 / 119 | 52 | 415/3 | 9.5 | 16 | 5.73/5.91 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
| PCA-RP140KAQ PUHZ-RP140VKA2 | 13.37 (6.2-15.3) | 9.89 | 9.05 | 3.10/3.27 | 16.0 (5.7-18.0) | 3.41/3.61 | 400-433-483-533 | 230 x 1600 x 680 | 39 | 41-43-45-48 | 1338 x 1050 x 330 | 120 / 121 | 52 | 240/1 | 28 | 40 | 17.17/19.23 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
| PCA-RP140KAQ PUHZ-RP140YKA2 | 13.37 (6.2-15.3) | 9.89 | 9.05 | 3.08/3.27 | 16.0 (5.7-18.0) | 3.39/3.61 | 400-433-483-533 | 230 x 1600 x 680 | 39 | 41-43-45-48 | 1338 x 1050 x 330 | 120 / 121 | 52 | 415/3 | 13 | 16 | 6.01/6.73 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | Optional*5 | Optional controller*7
Notes:
*1 - Nominal conditions cooling: EAT 27°CDB/19°CWB, Ambient 35°CDB | [9 empty] | *5 - Optional drain pump for PKA series: PAC-SH94DM-E
Rated conditions cooling: EAT 24°CDB/17°CWB, Ambient 35°CDB | [9 empty] | Optional drain pump for PCA-RP50 series: PAC-SH83DM-E | [14 empty] | Mitsubishi Electric is constantly developing and improving its products. The company reserves the right to make any variation in the technical specification to the equipment described, or to withdraw or replace products without prior notification. This is a guide only, please refer to the installation and service manuals to confirm the latest specifications or contact your local Mitsubishi Electric office.
Nominal conditions heating: EAT 20°CDB/15°CWB, Ambient 7°CDB/6°CWB | [9 empty] | Optional drain pump for PCA-RP71/100/125/140 series: PAC-SH84DM-E
*2 - Rated Load Amps (RLA) is based on nominal conditions. Use Maximum Circuit Amps (MCA) for power supply infrastructure sizing, etc. | [9 empty] | Optional drain pump for PCA-RP60 series: PAC-SH85DM-E
*3 - 3-core (3C) or 5-core (5C) electrical power supply cable to outdoor unit only, indoor unit is fed from outdoor unit. | [9 empty] | *6 - Facia for PLA-RP series (wireless option): PLP-6BALM
*4 - Single core double insulated (SDI) and Thermoplastic Sheated (TPS) twin and earth (2C+E) | [9 empty] | Facia for PLA-RP series (wired option): PLP-6BA (add wired controller PAR-31MAA or PAC-YT52CRA)
*7 - Wired controller option PAR-31MAA or PAC-YT52CRA (add terminal block PAC-SH29TC-E for PKA series)

## Mr Slim - Ducted
Model Reference |  | Cooling Performance |  |  |  | Heating Performance |  | Airflow |  | Indoor Unit |  |  |  |  | Outdoor Unit |  |  | Electrical | [6 empty] | Refrigerant | [5 empty] | Others |  | Guaranteed Operating Range
|  | Nominal Total Cooling*1 | Nominal Sensible Cooling*1 | Rated Sensible Cooling*1 | AEER/EER | Nominal Heating Capacity*1 | ACOP/COP | Airflow (Cooling/Heating) | Ext. Static Pressure | Dimensions (H x W x D) | Supply Spigot Size (H x W) | Return Spigot Size (H x W) | Weight | Noise Level (SPL/PWL) - in Cooling | Dimensions (H x W x D) | Weight | Noise Level (SPL/PWL) - in Cooling | Volt / Phase | MCA | MCB | RLA (Cooling/ Heating)*2 | Power Supply to IU | Power Supply to OU | IU/OU Connecting Wire | Pipe Size (Gas) OD | Pipe Size (Liquid) OD | Max Pipe Run | Max Lift | Pre-Charged R410A (Limit) | Add. Charge | Drain Pumps | Accessories | Indoor - Cooling | Indoor - Heating | Outdoor - Cooling | Outdoor - Heating
|  | kW | kW | kW |  | kW |  | L/s | Pa | mm | mm | mm | kg | dB(A) | mm | kg | dB(A) |  | A | A | A |  |  |  | mm (Inch) | mm (Inch) | m | m | kg | g/m |  |  | °CDB/°CWB | °CDB | °CDB | °CDB/°CWB
Compact Ceiling Concealed PEAD Series Power Inverter
| PEAD-RP71JAA SUZ-KA71VAD | 7.1 (0.9-8.1) | 5.9 | 5.6 | 3.33/3.38 | 8.0 (0.9-10.2) | 3.86/3.92 | 292-350-417 | 35-50-70-100-125 | 250 x 1100 x 732 | 178 x 1060 | 210 x 1058 | 29 | 30-34-39 | 880 x 840 x330 | 53 | 55 | 240/1 | 16.1 | 20 | 9.30/9.10 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 30 | 30 | 1.8 (7.0 m) | 55 | N/A | Optional controller | 21 / 15 to 32 / 23 | 20 to 27 | -10 to 43 | -10 / -11 to 24 / 18
| PEAD-RP71JAA PUHZ-RP71VHA5 | 7.3 (3.3-8.1) | 6.21 | 5.68 | 3.31/3.50 | 8.0 (3.5-10.2) | 3.78/4.00 | 292-350-417 | 35-50-70-100-125 | 250 x 1100 x 732 | 178 x 1060 | 210 x 1058 | 29 | 30-34-39 | 943 x 950 x 330 | 67 | 48 | 240/1 | 20.17 | 25 | 9.05/9.64 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 50 | 30 | 3.5 (30.0 m) | 600 per 10 m | N/A | Optional controller | 19 / 15 to 35 / 22.5 | 17 to 28 | -5 (-15) to 46 | -20 / -20 to 21 / 15
| PEAD-RP100JAA PUHZ-RP100VKA2 | 10.0 (4.9-11.4) | 8.74 | 7.99 | 3.34/3.61 | 11.2 (4.5-14.0) | 3.81/4.12 | 400-483-567 | 35-50-70-100-125 | 250 x 1400 x 732 | 178 x 1360 | 210 x 1358 | 38 | 33-38-42 | 1338 x 1050 x 330 | 118 | 51 | 240/1 | 26.5 | 32 | 12.64/13.58 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEAD-RP100JAA PUHZ-RP100YKA2 | 10.0 (4.9-11.4) | 8.74 | 7.99 | 3.31/3.61 | 11.2 (4.5-14.0) | 3.78/4.12 | 400-483-567 | 35-50-70-100-125 | 250 x 1400 x 732 | 178 x 1360 | 210 x 1358 | 38 | 33-38-42 | 1338 x 1050 x 330 | 119 | 51 | 415/3 | 8 | 16 | 4.42/4.75 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEAD-RP125JAA PUHZ-RP125VKA2 | 12.3 (5.5-14.0) | 10.37 | 9.48 | 3.14/3.33 | 14.0 (5.0-16.0) | 3.76/4.00 | 492-592-700 | 35-50-70-100-125 | 250 x 1400 x 732 | 178 x 1360 | 210 x 1358 | 39 | 36-40-44 | 1338 x 1050 x 330 | 118 | 52 | 240/1 | 26.5 | 32 | 16.36/16.90 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEAD-RP125JAA PUHZ-RP125YKA2 | 12.3 (5.5-14.0) | 10.37 | 9.48 | 3.11/3.33 | 14.0 (5.0-16.0) | 3.74/4.00 | 492-592-700 | 35-50-70-100-125 | 250 x 1400 x 732 | 178 x 1360 | 210 x 1358 | 39 | 36-40-44 | 1338 x 1050 x 330 | 119 | 52 | 415/3 | 9.5 | 16 | 5.73/5.91 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEAD-RP140JAA PUHZ-RP140VKA2 | 13.37 (6.2-15.3) | 11.9 | 10.88 | 3.09/3.32 | 16.0 (5.7-18.0) | 3.76/3.96 | 533-650-767 | 35-50-70-100-125 | 250 x 1600 x 732 | 178 x 1560 | 210 x 1558 | 43 | 40-44-49 | 1338 x 1050 x 330 | 120 | 52 | 240/1 | 28 | 40 | 17.17/19.23 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEAD-RP140JAA PUHZ-RP140YKA2 | 13.37 (6.2-15.3) | 11.9 | 10.88 | 3.07/3.32 | 16.0 (5.7-18.0) | 3.73/3.96 | 533-650-767 | 35-50-70-100-125 | 250 x 1600 x 732 | 178 x 1560 | 210 x 1558 | 43 | 40-44-49 | 1338 x 1050 x 330 | 121 | 52 | 415/3 | 13 | 16 | 6.01/6.73 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
Ceiling Concealed PEA Series Power Inverter
| PEA-RP100GAA PUHZ-RP100VKA2 | 10.0 (4.9-11.4) | 9.2 | 8.5 | 3.51/3.85 | 11.2 (4.5-14.0) | 4.11/4.46 | 560-700 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 39-42 | 1338 x 1050 x 330 | 118 | 51 | 240/1 | 26.5 | 32 | 12.64/13.58 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller | 19 / 15 to 35 / 22.5 | 17 to 28 | -5 (-15) to 46 | -20 / -20 to 21 / 15
| PEA-RP100GAA PUHZ-RP100YKA2 | 10.0 (4.9-11.4) | 9.2 | 8.5 | 3.51/3.85 | 11.2 (4.5-14.0) | 4.07/4.46 | 560-700 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 39-42 | 1338 x 1050 x 330 | 119 | 51 | 415/3 | 8 | 16 | 4.42/4.75 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEA-RP125GAA PUHZ-RP125VKA2 | 12.5 (5.5-14.0) | 11.5 | 10.6 | 2.98/3.15 | 14.0 (5.0-16.0) | 4.01/4.28 | 683-1000 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 42-45 | 1338 x 1050 x 330 | 118 | 52 | 240/1 | 26.5 | 32 | 16.36/16.90 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEA-RP125GAA PUHZ-RP125YKA2 | 12.5 (5.5-14.0) | 11.5 | 10.6 | 2.96/3.15 | 14.0 (5.0-16.0) | 3.98/4.28 | 683-1000 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 42-45 | 1338 x 1050 x 330 | 119 | 52 | 415/3 | 9.5 | 16 | 5.73/5.91 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEA-RP140GAA PUHZ-RP140VKA2 | 13.5 (6.2-15.3) | 12.2 | 11.2 | 3.06/3.22 | 16.0 (5.7-18.0) | 3.88/4.10 | 683-1000 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 42-45 | 1338 x 1050 x 330 | 120 | 52 | 240/1 | 28 | 40 | 17.17/19.23 | *3 | 3C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEA-RP140GAA PUHZ-RP140YKA2 | 13.5 (6.2-15.3) | 12.2 | 11.2 | 3.04/3.22 | 16.0 (5.7-18.0) | 3.86/4.10 | 683-1000 | 50-100-150 | 400 x 1400 x 634 | 250 x 921 | 330 x 1102 | 63 | 42-45 | 1338 x 1050 x 330 | 121 | 52 | 415/3 | 13 | 16 | 6.01/6.73 | *3 | 5C | SDI + TPS (2C+E)*4 | 15.88 (5/8) | 9.52 (3/8) | 75 | 30 | 5.5 (30.0 m) | 600 per 10 m | N/A | Optional controller
| PEA-RP170WJA PUHZ-RP170VKA2 | 16.45 (9.0-20.0) | 15.63 | 14.3 | 3.16/3.20 | 20.0 (9.5-22.4) | 3.22/3.33 | 833-1017-1200 | 60-75-100-150 | 470 x 1370 x 1120 | 340 x 1100 | 420 x 1100 | 108 | 38-41-44 | 1338 x 1050 x 330 | 127 / 131 | 76 | 240/1 | 34 | 40 | 19.4/23.9 | 3C | 3C | SDI + TPS (2C+E)*4 | 25.4 (1) | 9.52 (3/8) | 75 | 30 | 7.7 (30.0 m) | 900 per 10 m | N/A | Optional controller
| PEA-RP170WJA PUHZ-RP170YKA2 | 16.45 (9.0-20.0) | 15.63 | 14.3 | 3.16/3.20 | 20.0 (9.5-22.4) | 3.22/3.33 | 833-1017-1200 | 60-75-100-150 | 470 x 1370 x 1120 | 340 x 1100 | 420 x 1100 | 108 | 38-41-44 | 1338 x 1050 x 330 | 127 / 131 | 76 | 415/3 | 18 | 32 | 6.8/8.3 | 3C | 5C | SDI + TPS (2C+E)*4 | 25.4 (1) | 9.52 (3/8) | 75 | 30 | 7.7 (30.0 m) | 900 per 10 m | N/A | Optional controller
| PEA-RP200WJA PUHZ-RP200YKA2 | 19.44 (9.0-22.4) | 16.91 | 15.47 | 3.04/3.19 | 22.4 (9.5-25.0) | 3.12/3.25 | 833-1017-1200 | 60-75-100-150 | 470 x 1370 x 1120 | 340 x 1100 | 420 x 1100 | 108 | 38-41-44 | 1338 x 1050 x 330 | 136 | 76 | 415/3 | 19 | 32 | 8.2/9.7 | 3C | 5C | SDI + TPS (2C+E)*4 | 25.4 (1) | 9.52 (3/8) | 75 | 30 | 7.7 (30.0 m) | 900 per 10 m | N/A | Optional controller
| PEA-RP250WHA PUHZ-RP250YKM | 22.0 (11.2-27.0) |  |  | 3.27/3.60 | 25.0 (12.5-29.0) | 3.37/3.62 | 967-1183-1400 | 60-75-100-150 | 470 x 1370 x 1120 | 340 x 1100 | 420 x 1100 | 108 | 40-43-46 | 1650 x 920 x 760 | 200 | 58 | 415/3 | 23.8 | 32 | 9.7/11.1 | 3C | 5C | 1.5mm2 shielded | 22.2 (7/8) | 9.52 (3/8) | 75 | 30 | 9 | 600 g/m + 3.0 kg | N/A | Optional controller
Notes:
*1 - Nominal conditions cooling: EAT 27°CDB/19°CWB, Ambient 35°CDB
Rated conditions cooling: EAT 24°CDB/17°CWB, Ambient 35°CDB | [28 empty] | Mitsubishi Electric is constantly developing and improving its products. The company reserves the right to make any variation in the technical specification to the equipment described, or to withdraw or replace products without prior notification. This is a guide only, please refer to the installation and service manuals to confirm the latest specifications or contact your local Mitsubishi Electric office.
Nominal conditions heating: EAT 20°CDB/15°CWB, Ambient 7°CDB/6°CWB
*2 - Rated Load Amps (RLA) is based on nominal conditions. Use Maximum Circuit Amps (MCA) for power supply infrastructure sizing, etc.
*3 - 3-core (3C) or 5-core (5C) electrical power supply cable to outdoor unit only, indoor unit is fed from outdoor unit.
*4 - Single core double insulated (SDI) and Thermoplastic Sheated (TPS) twin and earth (2C+E)
Mitsubishi Electric is constantly developing and improving its products. The company reserves the right to make any variation in the technical specification to the equipment described, or to withdraw or replace products without prior notification. Refer to the product manual for further details.

## Sheet1
MXZ-2D52VA
MXZ-6C120VA
Maximum Refrigerant Piping Length
| Piping length each indoor unit (a, b, c, d, e, f) | 25 m
| Total piping length (a+b+c+d+e+f) | 80 m
| Max No. bends per unit | 25
| Total No. bends | 80